## Slide 1: Controller Tuning and Process Identification
Instrumentation and Process Control – ChE-323
Lec-12

## Slide 2: Controller Tuning and Process Identification
Controller tuning
  Adjustment of controller parameters to achieve satisfactory control
Process Identification
  Determining the model of a process experimentally

## Slide 3: Controller Types and Parameters
Proportional Controller
Proportional-Integral Controller
Proportional-Integral-Derivative Controller
Control Parameters
  Kc
  τI
  τD
Parameter selection is an optimization problem
  Satisfy criterion of optimality – good control
Optimization can be based on
  Trial and error
  Model based optimization

## Slide 4: Optimization criterion
For most cases, a process model is not available
  Criterion is vaguely defined
Typical criterion for good control
  Response to a step input has
    Minimum overshoot
    One-quarter decay ratio
  Minimum rise time - the time it takes for the system's output to transition from 10% to 90% of its final value in response to a step input
  Minimum settling time - the duration it takes for a system's output to reach and maintain a steady-state value within a specified tolerance band, typically within 2% or 5% of the final value

## Slide 5: Controller Tuning
Effect of PID controller modes
Second order process with transport lag
Considering a loop with second order process and measuring element as transport lag
Response of step change in load is tested with different control modes

## Slide 6: Controller Tuning
Effect of PID controller modes
Closed loop response to step change in set point
Closed loop response to step change in load

## Slide 7: Controller Tuning
Response of step change in load is tested with different control modes
  Well tuned responses are shown
  Integral action – eliminates offset
  Derivative action – speeds up the response
Effect of PID controller modes
Load response with different control modes

## Slide 8: Controller Tuning
Figure of merit
  A criterion that reduces the entire response to a single number
  Used to compare different control parameters
Nature of response and requirements for the process determine the “best” choice of parameters
Criteria for good control

## Slide 9: Controller Tuning
Integral of the square of error (ISE)
  With e as error
  (Set point – control variable)
  Objective is to minimize ISE
  If errors are large or persist for longer – ISE will be higher
Criteria for good control
Integral of the absolute value of error (IAE)
Integral of the time weighed absolute error (ITAE)

## Slide 10: Controller Tuning
Criteria for good control
Control criteria applied to PI control

## Slide 11: Controller Tuning
Criteria for good control
Control criteria applied to PI control
PI control Response

## Slide 12: Tuning Rules
Closed-loop tuning method
  Controller present and active
Ultimate gain Kcu and Ultimate period Pu are found by testing
Zeigler-Nicholas (Z-N) Rules

## Slide 13: Tuning Rules
After the process reaches steady state at the normal level of operation,
  remove the integral and derivative modes of the controller, leaving only proportional control.
  On some PID controllers, this requires that the integral time tI be set to its maximum value and the derivative time tD to its minimum value.
  On computer-based controllers, the integral and derivative modes can be removed completely from the controller.
Zeigler-Nicholas (Z-N) Rules

## Slide 14: Tuning Rules
Select a value of proportional gain Kc, disturb the system, and observe the transient response.
  If the response decays, select a higher value of Kc and again observe the response of the system.
  Continue increasing the gain in small steps until the response first exhibits a sustained oscillation.
  The value of gain and the period of oscillation that correspond to the sustained oscillation are the ultimate gain Kcu and the ultimate period Pu.
Zeigler-Nicholas (Z-N) Rules

## Slide 15: Tuning Rules
From the values of Kcu and Pu found in step 2, use the Ziegler-Nichols rules given in Table to determine controller settings (Kc, tI , tD ).
Zeigler-Nicholas (Z-N) Rules

## Slide 16: Tuning Rules
Open-loop tuning method
  Controller action removed
Manual mode used
Step change (M/s) signal sent to the valve introduces open loop transient
Cohen and Coon (C-C) Rules

## Slide 17: Tuning Rules
System response is called “Process Reaction Curve”
  Bu – ultimate value of measured variable
  Here gain is Kp
Cohen and Coon (C-C) Rules

## Slide 18: Tuning Rules
After the process reaches steady state at the normal level of operation, switch the controller to manual.
  In a modern controller, the controller output will remain at the same value after switching as it had before switching.
    This is called “bumpless” transfer.
    With the controller in manual, introduce a small step change in the controller output that goes to the valve and record the transient, which is the process reaction curve.
Cohen and Coon (C-C) Rules

## Slide 19: Tuning Rules
    Draw a straight-line tangent to the curve at the point of inflection.
      The intersection of the tangent line with the time axis is the apparent transport lag Td
      The apparent first-order time constant T is obtained from
Cohen and Coon (C-C) Rules

## Slide 20: Tuning Rules
Using the values of Kp, T, and Td from step 3, the controller settings are found from the relations given in Table.
Cohen and Coon (C-C) Rules